HazLoc LED LUMINAIRE

Installation and Maintenance Manual

Model L1719

Top Hi-Tech Co., Ltd.

9F, No.1, Zhongshan Road, Tucheng Dist. New Taipei City, 23680,236 Taiwan

Website: www.tht-ex.com

TEL: +886 2 2267-1234

FAX: +886 2 2269-1166

e-mail: sales@tht-ex.com

Pub. Code:

Subject to alterations

- General Information

Model L1719 LED Luminaires are suitable for use in the following hazardous (classified) areas as defined by the National Electrical Code (NEC) and Canadian Electrical Code (CEC):

- Class I, Division 2, Groups A, B, C, D

- Wet Locations (UL 1598)

Refer to the luminaire nameplate for specific classification information, maximum ambient temperature suitability and corresponding operating temperature (T-Code).

Model L1719 LED Luminaire is designed for using in indoors and outdoors environment.

Rated Voltage:

100/110/ 120/200/220/ 230/277/ 347/ 480Vac

Ambient Temperate Range: -40°C ~ +55°C and +65°C

____________________________________________________________________________________________

WARNING - To avoid the risk of fire, explosion or electric shock, this product should be installed, inspected and maintained by a qualified electrician only, in accordance with all applicable codes and regulations. - To avoid electric shock: - Be certain electrical power is OFF before and during installation and maintenance. - Luminaire must be supplied by a wiring system with an equipment grounding conductor. - To avoid explosion: - Make sure that the supply voltage is the same as the luminaire voltage. - Do not install where the marked operating temperatures exceed the ignition temperature of the hazardous atmosphere. - Do not operate in ambient temperatures above those indicated on the luminaire nameplate. - All gasket seals must be clean and undamaged. - Use proper supply wiring as specified on the luminaire nameplate. - Before dismounting, electrical power to the luminaire must be turned off. Keep tightly closed when in operation. - To avoid burning hands, ensure the luminaire is cool when performing maintenance.

____________________________________________________________________________________________

- Dimensions (All Dimensions in mm) – Subject to Alterations

- Technical Data

| Item | Description |
| --- | --- |
| Rated Voltage | 100/ 110/ 120/ 200/ 220/ 230/277/ 347/ 480 Vac |
| Watts | 240/ 280/ 300 Watts |
| Frequency | 50 & 60 Hz |
| Power Factor | cos φ ≧ 0.9 |
| Ambient Temperate Range | -40°C ~ +55°C -40°C ~ +65°C |
| Material Enclosure Glass | Aluminum alloy Heat and impact resistant tempered Glass |
| LED Service Life | 60,000 hrs |
| Mounting Type | WHT Mounting |
| Bending Electrical Tube Mounting |  |

- Assembly and Installation

  - Mounting Bracket Installation

    - WHT Mounting Bracket

- The mounting bracket is for the use of WHT mounting type.

- Suitable for installation on ceilings, walls, parapet walls.

- Position the bracket holders and fix it by means of the provided two to four M12 screws, 215.0 kgf-cm.

    - Bending Electrical Tube Mounting

- This mounting bracket type is for mounting unto the bending electrical tube.

- The assembly of the bracket onto the conduit must be secured with the use of M8 threaded screws and by applying 122.0 kgf-cm torque.

  - Putting into Service

Before putting into operating, it’s necessary to ensure that:

- the lighting is correctly installed.

- the connection has been correctly made.

- the wire has been inserted correctly.

- Maintenance

- To avoid personal injury, disconnect power to the light and allow the unit to cool down before performing maintenance.

- Perform visual, electrical, and mechanical inspections on a regular basis. The environment and frequency of use should determine this. However, it is recommended that checks be made at least once a year. Frequency of use and environment should determine this. It is recommended to follow an Electrical Preventive Maintenance Program as described in the National Fire Protection Association Bulletin NFPA No. 70B: Recommended Practice for Electrical Equipment Maintenance.

- The lens should be cleaned periodically to ensure continued lighting performance. Clean the lens with a clean, damp, non-abrasive, lint-free cloth. If this is not sufficient, use a mild soap or a liquid cleaner. Do not use an abrasive, strong alkaline or acid cleaner as damage may occur.

- Inspect the cooling fins on the luminaire to ensure that they are free of any contamination (i.e. excessive dust build-up). Clean with a non-abrasive cloth if needed.

- Electrically check to make sure that all connections are clean and tight.

- Mechanically check that all parts are properly assembled.

- Transport, Storage and Disposal

- Transport and storage is only allowed in the original packaging, on the way pointed out on the carton box.

- Transport – Shock-free in its original carton, do not drop, and handle carefully.

- Store – Store in a dry place in its original packaging.

- Disposal – Ensure environmentally friendly disposal of all components according to the legal regulations.